**Mycom Reciprocating compressor**

**5.3.1 Compressor Overhaul Interval and Operation Conditions**

The recommended overhaul interval is shown in the table below as a guideline. Preconditions (1) The operation conditions are within the specified range of use. (2) Number of start/stop cycles is within the specified range. Rotation speed is higher than 1200min-1, (3) Valve plate is “N3” type. (4) Discharge valve cage is “T1” type.

Table 5-5 Guideline for the overhaul interval Rotation Speed (N) Range (min-1) Overhaul interval

800≤N<1200 Whichever comes first: Operation time of 16000 hours or 2 years

1200≤N<1500 Whichever comes first: Operation time of 8000 hours or 2 years